## Background
GMLC Grid Services Master List v4 June 23, 2017
A number of the GMLC projects are concerned with grid operations, grid control, and use of new technologies. In particular, the use of Distributed Energy Resources and grid connected devices of various kinds that are not part of the usual utilty asset base are being considered for supplying existing or possible new grid services. The basic starting definition of grid services comes from FERC. FERC defines the ancillary services as: "those services necessary to support the transmission of electric power from seller to purchaser given the obligations of control areas and transmitting utilities within those control areas to maintain reliable operations of the interconnected transmission system." We extend this to include support for reliable distribution system operations as well. In order to provide a degree of coordination on this topic across the GMLC, this document is a compilation of functions (cast as services) that could support grid operation. Some are presently recognized as grid services in the sense that the are defined by NERC as essential reliability services (formerly known as ancillary services) and /or are presently procured by system operators or utilities in various ways. Others are services that are being proposed or developed but may not yet be in wide use. In a few cases, functions are listed that may be difficult to unbundle as services but are present for completeness and are so noted. This list does not include IT-type services, such as Cloud-based data management or analytics, or communication network management. The list does not presume any particular view of how the grid should evolve or should be operated; those views will come from other GMLC activities and the industry. The limited purpose of this list is to provide the GMLC projects a common reference set of grid support services.
The Master List tab has the consolidated and organized grid services list. The other tabs contain reference information and some detail related to frequency regulation.
The list was compiled from a number of sources, and the GMLC PIs were asked to review and comment. The feedback has been incorporated into this document. After further review, it was decided to augment the spreadsheat with additional explanatory information at the sub -category level.
Some reference materials used in this work:
Ancillary Services; Technical and Commercial Insights, Brendan Kirby, Wartsila, July 2007.
Essential Reliability Services Task Force Measures Framework Report, NERC, November 2015
A Concept Paper on Essential Reliability Services that Characterizes Bulk Power System Reliability, NERC, October 2014
Standards for Imports of Regulation, CA ISO, November 2012
Electric Power Ancillary Services, ORNL, February 1996
Frequency Response Phase 2 Issue Paper, CA ISO, December 2016
CPUC Competitive Solicitation Working Group Distribution Services
A Framework to Make the Distribution Grid More Open, Efficient and Resilient, More Than Smart & Resnick Institute,
Energy Storage for the Electricity Grid: Benefits and Market Potential Assessment Guide, Sandia National Laboratory, February 2010.

## Master List
[5 empty] | Grid Services | Must Provide Service | Description | Grid Objective | Time Frame | Requestor(s) | Provider(s) | Other Remarks
Organization Key:
Group
Category
Subcategory
Grid Service Name
No.
| 1 |  | Scheduling
|  | 1.1 |  |  | Production Coordination |  | Process of committing generation to meet system load while minimizing the total production cost, while considering the avoidable fixed costs, such as start-up, shut-down, no-load costs, etc. | Ensure enough resources are committed to meet system load, as well as ancillary services, while meeting generation, transmission, and other system constraints, including N-1 security conditions | Week- to day-ahead, hour-ahead | Market participants - generators, load serving entities, and transmission owners | ISO/RTO (independent system operator / regional transmission organization)
|  |  | 1.1.1 |  | Production Optimization
1 |  |  |  | 1.1.1.1 | Unit Commitment | Yes
|  |  |  | 1.1.1.2 | Energy Scheduling | Yes | [5 empty] | Can be done in several ways; the most common is economic dispatch
|  |  | 1.1.2 |  | Wheeling | Yes | [5 empty] | Power transfer through a service area or out of a service area
|  | 1.2 |  |  | Dispatch /Balance |  | *Process of determining commitment/decommitment of peaking units *Process of determining generation dispatch points based on the unit commitment schedules; *Dispatch process also determines market prices for energy and ancillary services. | Least-cost dispatch to ensure achievement of load balancing, as well reserves for ancillary services, while managing transmission congestion | Intra-hour up to 5 minute | Market participants - generators, load serving entities, and transmission owners | ISO/RTO
|  |  | 1.2.1 |  | Generation-Load Matching (load following) / Meet Energy Imbalance by Generation Change | [6 empty] | Corrections for residual deviations from schedule and forecast
|  |  |  | 1.2.1.1 | Redispatch | Yes | [5 empty] | Redispatch units from DA schedules; this could be for an EIM (energy imbalance market) or simply load following up and down for a vertically integrated utility
10 |  |  |  | 1.2.1.2 | Wind and Solar Curtailment
|  |  | 1.2.2 |  | Demand Modification
|  |  |  | 1.2.2.1 | Peak Demand Limiting | No | [5 empty] | Traditionally via DR (demand response), but more generally via DER (distributed energy resources)
5 |  |  |  | 1.2.2.2 | Energy Shifting (Net Load Adjustment) | No | [5 empty] | Traditionally via DR, but more generally via DER
|  | 1.3 |  |  | Energy Settlements | Yes | Payments for energy production, consumption and losses based on actual metering | Multi-settlement process to determine financial charges and credits to market participants based on their participation in the financial transmission rights, day-ahead energy and operating reserves, and real-time energy and operating reserves markets | Post-real time | Market participants - generators, load serving entities, and transmission owners | ISO/RTO
|  |  | 1.3.1 |  | Interchange
|  |  | 1.3.2 |  | Loss Compensation
|  |  | 1.3.3 |  | Uninstructed/Instructed Deviation of Generation
| 2 |  | Regulation and Stabilization
|  | 2.1 |  |  | Frequency Support | [6 empty] | Frequency regulation exists to deal with residual imbalance effects, not primary balance
|  |  | 2.1.1 |  | Inertial Support and Damping | Yes | Consists of response components provided by system inertia | The need for adequate grid dynamic response during disturbances, such as faults or loss of large load or generator | Subsecond | BA/ISO/RTO | Owners of all committed machines and devices (DER) at different power plants/substations within the BA (balancing authority), stabilizers | Inertia responds to df/dt (ROCOF - rate of change of frequency); damping responds to Df but very fast
|  |  |  | 2.1.1.1 | Primary System Inertia | [5 empty] | Required by grid code in interconnection contract | Limits initial Df until governors take over and also stabilizes load sharing via droop
15 |  |  |  | 2.1.1.2 | Inertia Augmentation | [6 empty] | Adds inertia via DER and other methods to replace loss of inertia due to generator mix changes
|  |  |  | 2.1.1.3 | Inertia Modulation | [6 empty] | For compensating variable inertia and for increasing maneuverability (ability to adjust grid state)
|  |  |  | 2.1.1.4 | Damping | [6 empty] | Typically load-based modification of real power flow in response to locally sensed frequency; may operate very fast
|  |  | 2.1.2 |  | Primary | Yes | Consists of response components provided by system load, and generators’ speed governors. | The need for adequate grid dynamic response during disturbances, such as faults or loss of large load or generator | Seconds to tens of seconds | BA/ISO/RTO | Owners of all committed machines and devices (DER) at different power plants/substations within the BA | Responds to Df
|  |  |  | 2.1.2.1 | Droop/Governor Response | [6 empty] | Traditionally also involves regulation reserves
|  |  |  | 2.1.2.2 | Load Modification | [6 empty] | Includes modification of apparent load power
|  |  | 2.1.3 |  | Secondary | Yes | Provided by units on AGC (automatic generation control) | To maintain grid frequency, and to honor scheduled energy flows between different BAs. It is measured through NERC CPS1, CPS2 (retired), and the new BAAL (balancing authority area control error limit) score requirements | From tens of seconds to 5-15 minutes | BA/ISO/RTO | Owners of all committed machines and devices (DER) at different power plants/ substations within the BAs that are approved by the requestor to provide AGC (automatic generation control) capabilities | Responds to Df and imbalance
20 |  |  |  | 2.1.3.1 | Regulation Up | [6 empty] | Traditionally done via synchronized (spinning) and supplemental reserves
|  |  |  | 2.1.3.2 | Regulation Down | [6 empty] | Traditionally done via synchronized (spinning) and supplemental reserves
|  |  |  | 2.1.3.3 | Load Modification | [6 empty] | Net change in apparent load; can include DER effects or load shed
|  |  | 2.1.4 |  | Tertiary |  | Tertiary balancing service is provided by the spinning and non-spinning reserve units. | To maintain scheduled energy flows between different BAs, to maintain the BA generation-load balance (load-following reserve). To maintain grid reliability under N-1 contingencies (spinning and non spinning reserve). | From 5-15 minutes to 30 minutes or longer if replacement is through market response | BA/ISO/RTO | Committed synchronous machines at different power plants that are approved by the requestor to provide load-following service and that have the most economical bid or energy price to be dispatched in markets or vertically integrated utilities. | Restore generation-load equilibrium for long term
|  |  |  | 2.1.4.1 | Replacement | [6 empty] | Traditionally done with contingency reserves
|  |  |  | 2.1.4.2 | Market Responses | [6 empty] | Procure new replacement generation on short notice
25 |  |  |  | 2.1.4.3 | Load Modification | [6 empty] | Net change in apparent load; can include DER effects or load shed
|  | 2.2 |  |  | Voltage Support | Yes | Provide voltage control by delivering or absorbing reactive power, changing transformer tap settings, adjusting regulators, using capacitor banks | To maintain grid voltage stability, generator buses at scheduled voltage level and load buses within prespecified maximum and minimum voltages | Real time | BA/ISO/RTO/DO, compliance with NERC and regional standards | Power plants, SVCs (static var compensators), statcoms (static synchronous compensators), D-VARs (dynamic reactive power compensators), capacitor banks, inductor banks, transformer taps, voltage regulators, DG smart inverters
|  |  | 2.2.1 |  | Voltage Adjustment
|  |  |  | 2.2.1.1 | Bulk System Voltage Regulation | [6 empty] | Regulation at bulk generators, for example
|  |  |  | 2.2.1.2 | Distribution-Level Voltage Regulation | [6 empty] | OLTCs (on-load tap changers), voltage regulators, serial line drop compensators, for example; may not be possible to unbundle
|  |  |  | 2.2.1.3 | Edge-Device Voltage Regulation Support | [6 empty] | Typically DER rather than utility grid devices such as in 2.2.1.2
|  |  | 2.2.2 |  | Reactive Power Control
|  |  |  | 2.2.2.1 | Bulk System Var Regulation | [6 empty] | Generator and synchronous condenser control, for example
30 |  |  |  | 2.2.2.2 | Distribution-Level Var Regulation | [6 empty] | Capacitor banks, for example; may not be possible to unbundle or monetize, although some schemes have been proposed
|  |  |  | 2.2.2.3 | Edge Device Var Regulation Support | [6 empty] | Typically DER rather than utility grid devices such as in 2.2.2.2
|  | 2.3 |  |  | Ramping |  | Flexibility product/service in MW/min (rate of power change) that is typically acquired from committed resources that have been dispatched above their no-load levels | Ensure acquisition of enough resources to provide flexibility to deal with known and unknown sources of uncertainty, typically uncertain wind and solar forecasts | Real time | ISO/RTO | Generators, responsive loads, energy storage resources, etc. | Ramping may be up or down (CA duck curve, late afternoon solar is ramping down and load is ramping up). Fast ramping of wind in MISO resulted in price spikes due to insufficient flex units on line
|  |  | 2.3.1 |  | Ramp Response | Yes, in some regions
|  |  |  | 2.3.1.1 | Generation Dispatch
|  |  |  | 2.3.1.2 | Storage Dispatch | [6 empty] | Grid scale or aggregated, for example
|  |  |  | 2.3.1.3 | Load Modification | [6 empty] | Load may be decreased (typical) or increased (being considered at CA ISO)
| 3 |  | Miscellaneous
|  | 3.1 |  |  | Measurement and Forecast |  | Grid state and situational awareness (environmental) | Data acquisition for support of grid planning, operation, and market | Real time to years ahead | BA/ISO/RTO/utilities | Meters, SCADA (supervisory control and data acquisition), PMUs (phasor measurement units) and DER (distributed energy resources) | DER can provide grid data as a by-product (such as voltage and frequency) we should consider if that would be deleted
|  |  | 3.1.1 |  | Bulk Energy System
35 |  |  |  | 3.1.1.1 | Tie-Line Telemetry | [6 empty] | Tie-lines connect balancing-authority areas or fully metered electric system regions
|  |  |  | 3.1.1.2 | Synchronized Grid State Data Sharing Between Different BAs/RTOs | [6 empty] | Typically PMU data; may also include line sensing, fault metering, etc.
|  |  | 3.1.2 |  | Distribution
|  |  |  | 3.1.2.1 | Electric Metering | [6 empty] | Load consumption
|  |  |  | 3.1.2.2 | Auxiliary Metering | [6 empty] | Zone metering, pass-through of water, gas metering
|  |  |  | 3.1.2.3 | Production Metering | [6 empty] | For distributed generation
|  |  | 3.1.3 |  | Environmental
40 |  |  |  | 3.1.3.1 | Weather - Actual and Forecast | [6 empty] | Temperature, precipitation, including icing
|  |  |  | 3.1.3.2 | Insolation - Actual and Forecast
|  |  |  | 3.1.3.3 | Wind - Actual and Forecast
|  |  |  | 3.1.3.4 | Lightning - Actual and Forecast
|  |  |  | 3.1.3.5 | Water Flow - Actual and Forecast | [6 empty] | For example, river flow rates and tides
|  | 3.2 |  |  | Other | [6 empty] | http://www.electropedia.org/iev/iev.nsf/display?openform&ievref=614-01-01
|  |  | 3.2.1 |  | Power Quality Support |  | Services that help to mange power quality, which is defined as characteristics of the electric current, voltage, and frequency at a given point in an electric power system, evaluated against a set of reference technical parameters | The electric energy delivered to the consumer must satisfy power quality requirements; for example, flicker and harmonics should be within acceptable levels. | Real time | Utilities on behalf of consumers | Utilities, energy service organizations (aggregators, DER owners)
|  |  |  | 3.2.1.1 | Harmonics and Distortion Management
|  |  |  | 3.2.1.2 | Steady-State Voltage and Unbalance Management
|  |  |  | 3.2.1.3 | Fast Transient Compensation, Transmission | [6 empty] | Traditionally done with FACTS (flexible AC transmission system device); could be fast storage; reacts on a sub-cycle time scale
55 |  |  |  | 3.2.1.4 | Fast Transient Compensation, Distribution | [6 empty] | Done in some places with DSTATCOM (distributed static compensator); could be fast DG/DS (distributed generation/distributed storage); reacts on a sub-cycle time scale
|  |  | 3.2.2 |  | Reliability/Resilience Support |  | The ability of a power system to meet its supply function under stated conditions for a specified period of time | Minimize electric service interruption to consumers | Short- and long-term planning | NERC, through its regional entity such as WECC | BA/ISO/RTO/utilities | For all hazards, including attack, http://www.electropedia.org/iev/iev.nsf/display?openform&ievref=603-05-02, island of microgrid during UFLS for example
|  |  |  | 3.2.2.1 | Outage Frequency and Duration Reduction
|  |  |  | 3.2.2.2 | Restoration Support
|  |  |  | 3.2.2.3 | Outage Ride-Through | [6 empty] | For critical loads
|  |  |  | 3.2.2.4 | System Integrity Protection Support
|  |  | 3.2.3 |  | Risk Reduction
|  |  |  | 3.2.3.1 | Safety | [6 empty] | For example, detect/isolate high impedance faults and stray voltages
60 |  |  |  | 3.2.3.2 | Supply Diversity | [6 empty] | Mitigate supply assurance risks
|  |  | 3.2.4 |  | System Support
|  |  |  | 3.2.4.1 | Black-Start Services |  | The ability of a power plant to self-start without electricity from the grid | To restore electric services after a blackout |  | BA/ISO/RTO/utilities | Power plants with black-start capability | Control DER to assist black start
|  |  |  | 3.2.4.2 | Time Correction | [6 empty] | Adjust system frequency for time-standard reasons

## Standard Services Raw Lists
This sheet contains standard definition of services as used in the electric utility industry. They are derived from regulatory and other industry sources and generally derive from Bulk Energy Systems operations.
SERVICES | SERVICES | COMMENTS
NERC Essential Reliability Services | NERC Interconnected Operating Services
Frequency Support | Frequency Response | See the Freq Regulation Details tab for some key specifications
Inertial support |  | Traditionally derives from rotational momentum of traditional generators; acts instantaneously to slow initial ROCOF; note that as wind and solar displace traditional generation, system inertia provided by such units decreases. See Proposed services for more info.
Primary freq response (droop and governor response) |  | Operates in the roughly 5-30 second time range after a system frequency change via localized control; load sharing adjustment is stabilized by system inertia to minimize/prevent governor hunting.
Secondary freq response – AGC/ACE | Regulation Load following | Operates in the 30-second to ten minute time period after a frequency change; traditionally done via centralized control at Balancing Authorities or system operators. Some ISOs use market mechanisms to procure resources for regulation. Generation capacity above the nominal generation level is called ‘regulation up’ and below is called ‘regulation down’. Regulation up and regulation down are procured as separate ancillary services in California. | s
Tertiary freq response | Contingency Reserve | Operates in the 30 + minute range to replace secondary response using manual supplemental reserve or market dispatch.
Voltage Support | Reactive Power Supply from Gen Sources | The primary objective of Voltage Support is to maintain the voltages in the transmission system within a secure, stable range. Voltage support is specific and requires reactive power control from reactive resources distributed throughout the power system.
Ramping
System Black Start Capability
FERC Ancillary Services | Other BES Services
Reactive power / voltage control | Responsive reserve
Loss Compensation | Spinning reserve
Scheduling and dispatch | Planning reserve
Load following | Scheduled backup
System protection | Wheeling
Energy imbalance | Tie line telemetry
Emergency energy
Inadvertent energy payback
Redispatch
PMU data sharing
Traditional Ancillary Reserves Taxonomy

## Proposed Services Raw Lists
This sheet contains definitions of proposed services. In many cases the services are the same as those on the Standard Services page, but the method of delivering them is non-traditional (from DER for example).
SERVICES or Values | COMMENTS | SERVICES or Values | COMMENTS
CPUC Competitive Solicitation Working Group Distribution Services
Distribution Capacity services | Load modifying or supply services that DERs provide via dispatch of output (MW) or reduction in load that is capable or reliably and consistently reducing net loading on desired distribution infrastructure.
Voltage support via real and reactive power control | Improved steady-state voltage to avoid voltage related investment. Dynamic voltage management to keep secondary and primary voltage within interconnection rule limits.
Reliability services | Load modifying or supply service capable of improving local distribution reliability and/or resiliency. Service provides fast reconnection and availability of excess reserves to reduce demand when restoring customers to service during abnormal configurations.
Resilience services | Load modifying or supply service, including microgrids, capable of improving local distribution reliability and/or resiliency. Service provides fast reconnection and availability of excess reserves to reduce demand when restoring customers to service during abnormal configurations. Service also provides power to islanded end-use customers when central power is not supplied and thus reduce the duration of outages.
CA More Than Smart DER Value Components | These are not explicitly services but can imply services to deliver the values listed. | Sandia NL Storage Values | These are not explicitly services but can imply services to deliver the values listed.
Regional Bulk Power System Benefits | Regional BPS benefits not reflected in System Energy Price or LMP | Electric Energy Time-shift | Depends on energy price differential, storage efficiency, and storage variable operating cost.
System Energy Price | Estimate of marginal wholesale system-wide value of energy | Electric Supply Capacity | Peak demand hours
Wholesale Energy | Reduced quantity of energy produced based on net load | Load Following | Assume: 1 hour of discharge duration provides approximately 2 hours of load following.
Resource Adequacy | Reduction in capacity required to meet Local RA and/or System RA | Area Regulation | Based on demonstration of Beacon Flywheel.
Flexible Capacity | Reduced need for resources for system balancing | Electric Supply Reserve Capacity | Allow time for generation-based reserves to come on-line.
Wholesale Ancillary Services | Reduced system operational requirements for electricity grid reliability | Voltage Support | Time needed for a) system stabilization or b) orderly load shedding.
RPS Generation & Interconnection Costs | Reduced RPS energy prices, integration costs, quantities of energy & capacity | Transmission Support | Per EPRI-DOE Handbook of Energy Storage for Transmission and Distribution Applications.
Transmission Capacity | Reduced need for system & local area transmission capacity | Transmission Congestion Relief | Peak demand hours. Low value is for "peaky" loads, high value is for "flatter" load profiles.
Transmission Congestion + Losses | Avoided locational transmission losses and congestion | T&D Upgrade Deferral 50th percentile | Same as Above
Wholesale Market Charges | LSE specific reduced wholesale market & transmission access charges | T&D Upgrade Deferral 90th percentile | Same as Above
Subtransmission, Substation & Feeder Capacity | Reduced need for local distribution upgrades | Substation On-site Power | Per EPRI/DOE Substation Battery Survey.
Distribution Losses | Value of energy due to losses bet. BPS and distribution points of delivery | Time-of-use Energy Cost Management | Peak demand hours.
Distribution Power Quality + Reactive Power | Improved transient & steady-state voltage, harmonics & reactive power | Demand Charge Management | Maximum daily demand charge hours, per utility tariff.
Distribution Reliability + Resiliency | Reduced frequency and duration of outages & ability to withstand and recover from external threats | Electric Service Reliability | Time needed for a) shorter duration outages or b) orderly load shutdown.
Distribution Safety | Improved public safety and reduced potential for property damage | Electric Service Power Quality | Time needed for events ride through depends on the type of PQ challenges addressed.
Customer Choice | Customer & societal value from robust market for customer alternatives | Renewables Energy Time-shift | Depends on energy cost/price differential and storage efficiency and variable operating cost.
Emissions (CO2, Criteria Pollutants & Health Impacts) | Reduction in state and local emissions and public and private health costs | Renewables Capacity Firming | Low & high values for Renewable Gen./Peak Load correlation (>6 hours) of 85% & 50%.
Energy Security | Reduced risks derived from greater supply diversity | Wind Generation Grid Integration, Short Duration | For a) Power Quality (depends on type of challenge addressed) and b) Wind Intermittency.
Water & Land Use | Synergies with water management, environmental benefits & property value | Wind Generation Grid Integration, Long Duration | Backup, Time-Shift, Congestion Relief.
Economic Impact | State or local net economic impact (e.g., jobs, investment, GDP, tax income)